## Sheet1
Fountain Valley Power
Gas Turbine Procurement Agreement Guarantees and LDs | [5 empty] | 2001-01-10
| Number of Units |  | 6
Guarantee |  |  | Each Unit
| Gross Power | kW | 41300 |  | Guarantee data Sheet
| GT Auxiliaries | kW | 265
| Net Power | kW | 41035 | 10.7.1 (delete 10.7.3)
| Gross Heat Rate | Btu/kWhr LHV | 8859 |  | Guarantee data Sheet
| Net Heat Rate | Btu/kWhr LHV | 8916.2106 | 10.8.1
Specific Performance |  |  | Allowance |  |  | Delta
| Net Power | kW | 4% | 39393.6 | 10.7.2 | 1641.4
| Net Heat Rate | Btu/kWhr LHV | 4.414% | 9327.9461 | 10.8.3 | 411.7355 | (Lee used 4.5%)
LD Calculations |  |  |  |  | Caculated | LD Cap
|  |  | 0-1804 kW | Max unit LD | Max facility LD | 10%
| Net Power | $/kW | 250 | 410350 | 2462100 | 8646425 | per 10.10.4/5
| Net Heat Rate | $/B/kWh LHV | 3500 | 1441074.3918 | 8646446.351 | 8646425 | and 1.56
Power Specific Performance allowance equal to value in original purchase agreement
Heat Rate Specific Performance allowance calculated to equal LD Cap (less than 4.5% in original purchase agreement)
Note. Example in 10.9.1 of the Procurement Agreement contains an example with mathematical errors.
The example calculates the per-unit damages, but incorrectly neglects to multiply the per unit value by 6,
dispite its inclusion in the equation. This should be revised to remove doubt about the clarifying equations.